## Complete feedback
Market participant | Topic | Reference | Question/remark | Baltic TSO response | TSO actions
Eesti Energia | General overview of the prequalification steps provided in chapter 2. Is the process acceptable for market participants? | 2 | As a market participant, we would like to stress that strictly only as a last resort measure it is acceptable to procure balancing reserves from TSO’s assets. However, provided that Reserve Units owned and operated by a TSO are eligible to participate in providing the balancing services, does the TSO need to prequalify these Reserve Units? Who will decide whether these assets fulfil the requirements? | Yes, TSO resources shall follow the same prequalifcation tests and need to fulfil the same requirements as other Reserve Units. TSO shall assess these requirements. It is the TSOs obligation to ensure that the connected Reserve Units are capable of providing reserves according to the requirements as TSO needs to use these to keep the balance of the system. | Baltic TSOs have provided clarification
Anonymous | General overview of the prequalification steps provided in chapter 2. Is the process acceptable for market participants? | 2 | Figure 1. When is the very beginning (start) date of stage no.1 (BSP submission of applications) which duration is measured by 8 weeks? | The 8 week time period starts with the BSP submission of the application to the TSO to review. TSO has up to 8 weeks to review the application. Baltic TSOs do not wish to prolong the process and will act as quick as possible. The time periods are defined according to SOGL Articles 155.3, 155.4, 159.3 and 159.4 | Document has been updated
Eesti Energia | Data exchange requirements provided in chapter 2.3. | 2 | Requirements for real-time communication need to be specified. With reference to Directive 2019/944 Article 17 Section 2, we propose that for technical reasons, real-time communication (once in 10 seconds) is only required for assets >=1,5 MW. For assets <1,5 MW (DSR based Reserve Units and RPGs), communication between TSO and aggregator’s VPP can be once in 10 seconds, but the information about the assets in the portfolio (when required) can be refreshed once in 1-15 min time periods. | Real-time requirements are according to SOGL Article 50(1), 154(8), 154(9) and 158(1)(e). Reserves providing units or a reserve providing group shall be monitord on real-time measurements. Aggregated assets in RPU or RPG shall provide aggregated real-time measurement, but individual assets in the RPG or RPU that are below 1,5 MW do not need to have real-time data exchange established, but timestamped data will be collected. | Document has been updated
Anonymous | Data exchange requirements provided in chapter 2.3. DISAGREE | 2 | We propose to add the following paragraphs: “Real-time communication requirements set individually by the connecting TSO shall be published (be available for BSR) prior to LFC prequalification process”. “Data exchange between the individual individual BSR and TSO shall be treated as confidential” | TSOs agree with the proposal, but make the remark that aggregated data per TSO may be collected and shared between Baltic TSOs. | Document has been updated
Eesti Energia | Information required in the prequalification application provided in chapter 2.1. Is the information required from the market participant understood or additional clarification is needed on the information points? | 2 | The requirements under 2.1.4. to provide the full list of technical entities for RPU and RPG are rather impossible to fulfil before application submission, because the actual set of assets (Reserve Providing Unit) used during the test and while providing the service can constantly change depending on weather, demand side resource availability etc. With reference to Directive 2019/944 Article 17 Section 2, we propose using the same approach and wording as for Elering-Fingrid aFRR pilot (Standard contract and Appendix 1. | As different DSR models are being developed and used in Baltics and in Europe in general, Baltic TSOs agreed that DSR management shall be subject to requirements in the national terms and conditions. | Baltic TSOs have provided clarification
Eesti Energia | Information required in the prequalification application provided in chapter 2.1. Is the information required from the market participant understood or additional clarification is needed on the information points? | 2 | Regarding 2.1.5: We propose that for Reserve Providing Groups such as VPP portfolios, the Delivery point is located at the portfolio itself. | Baltic TSOs disagree and see that each RPU or technical entity within RPG shall have a delivery point that shall follow the real-time requirements according to SOGL Article 50(1), 154(8), 154(9) and 158(1)(e). Reserves providing units or a reserve providing group shall be monitord on real-time measurements. Aggregated assets in RPU or RPG shall provide aggregated real-time measurement, but individual assets in the RPG or RPU that are below 1,5 MW do not need to have real-time data exchange established, but timestamped data will be collected. | Baltic TSOs have provided clarification
Eesti Energia | General overview of the prequalification steps provided in chapter 2. Is the process acceptable for market participants? | 2 | 5.3: We would like to indicate that even if the TSO rejects the Reserve Unit due to some reasoning, it must be possible for that Reserve Unit to apply for another prequalification test. | A Reserve Unit that has been rejected may apply for a repeated prequalification test, following the same procedure, and must indicate measures taken to correct the TSO highlighted reasoning for rejection (Ch. 2.1, p. 5.4) from the previous testing. | Baltic TSOs have provided clarification
Eesti Energia | Information required in the prequalification application provided in chapter 2.1. Is the information required from the market participant understood or additional clarification is needed on the information points? | 2 | Please provide the document list in 2.2. “Service agreement requirement and national terms and conditions”. | The service agreement and national terms and conditions shall be developed for each TSO after the finalised Baltic harmonised LFC reserve prequalifcation principles. | Baltic TSOs have provided clarification
Eesti Energia | Timeline presented in prequalification process provided in chapter 2.1. Are the time periods presented in the prequalification process acceptable? | 2 | 8 week time period for the review of application seems to be too long. Instead, we propose 2 weeks. | Baltic TSOs do not wish to prolong the process and will act as quick as possible. The time periods are defined according to SOGL Articles 155.3, 155.4, 159.3 and 159.4 | Baltic TSOs have provided clarification
Eesti Energia | Timeline presented in prequalification process provided in chapter 2.1. Are the time periods presented in the prequalification process acceptable? | 2 | 12 week period for test results review seems to be too long. Instead, we propose 4 weeks. | Baltic TSOs do not wish to prolong the process and will act as quick as possible. The time periods are defined according to SOGL Articles 155.3, 155.4, 159.3 and 159.4 | Baltic TSOs have provided clarification
Eesti Energia | General overview on the prequalification requirements provided in chapter 2.2. | 2 | We suggest amending the section so that Reserve Units and assets in Reserve Providing Units/Groups that are connected to DSO network such as DSR assets, which have not passed any grid acceptance tests etc., are also eligible to provide the balancing services. | Reserve Units connected to DSO are eligble to provide balancing services if they are able to successfully complete prequalication process. | Baltic TSOs have provided clarification
Eesti Energia | General overview on the prequalification requirements provided in chapter 2.2. | 2 | Regarding reassessment: it should be possible for DSR assets under VPP portfolio umbrella to provide balancing services according to Directive 2019/944 Article 17 Section 2: “Member States shall ensure that transmission system operators and distribution system operators, when procuring ancillary services, treat market participants engaged in the aggregation of demand response in a non-discriminatory manner alongside producers on the basis of their technical capabilities”. Therefore, we suggest adjusting or amending the clauses 2 and 3 so that the DSR assets in the VPP portfolio can be changed or replaced during the 5 year period, and it would not require automatic reassessment. | As different DSR models are being developed and used in Baltics and in Europe in general, Baltic TSOs agreed that DSR management shall be subject to requirements in the national terms and conditions. | Baltic TSOs have provided clarification
Fusebox | General overview of the prequalification steps provided in chapter 2. Is the process acceptable for market participants? | 2 | Overview is good and easy to understand.Would be good to stress out the most important bullets separately for each product available for Reserve providers. | Baltic TSOs see that Baltic LFC concept document and the current document provide both general and detailed information overview for each service types. | Baltic TSOs have provided clarification
Fusebox | Information required in the prequalification application provided in chapter 2.1. Is the information required from the market participant understood or additional clarification is needed on the information points? | 2 | This is something where TSO and Reserve Provider could have a stronger cooperation. In chapter 2.1.5. TSOs should share connection point/delivery point data if it is available to them (eg. High Voltage). 2.1.4.3. better exchange of EIC codes between Reserve Provider and TSOs would reduce the entry barrier for many technical entities. | BSP submitting the application shall have the full list of Z EIC codes and available W EIC codes for the technical entities within Reserve Unit. DSR is subject of requirements in national terms and conditions that shall be developed by each TSO separately. | Baltic TSOs have provided clarification
Fusebox | Timeline presented in prequalification process provided in chapter 2.1. Are the time periods presented in the prequalification process acceptable? | 2 | 12 weeks to organize and validate prequalification tests is too long period. It might raise the costsfor aggregation of technical entities. | Baltic TSOs do not wish to prolong the process and will act as quick as possible. The time periods are defined according to SOGL Articles 155.3, 155.4, 159.3 and 159.4 | Baltic TSOs have provided clarification
Anonymous | General overview of the prequalification steps provided in chapter 2. Is the process acceptable for market participants? | 2 | It is not clear if TSO themselves (in case they own and operate BESS) shall follow the prequalification process described in the figure 1 and how to ensure non discriminative attitude from TSO side to all BSP in this case. | Yes, TSO resources shall follow the same prequalifcation tests and need to fulfil the same requirements as other Reserve Units. TSO shall assess these requirements. It is the TSOs obligation to ensure that the connected Reserve Units are capable of providing reserves according to the requirements as TSO needs to use these to keep the balance of the system. | Baltic TSOs have provided clarification
Ignitis | General overview of the prequalification steps provided in chapter 2. Is the process acceptable for market participants? | 2 | There is no procedure in place for repeating the qualification and assessment if a market participant fails to meet the qualification requirements on the first attempt. | A Reserve Unit that has been rejected may apply for a repeated prequalification test, following the same procedure, and must indicate measures taken to correct the TSO highlighted reasoning for rejection (Ch. 2.1, p. 5.4) from the previous testing. | Baltic TSOs have provided clarification
Ignitis | General overview on the prequalification requirements provided in chapter 2.2. | 2 | Please specify more in detailed way the process of re-assessment. Who and when shall apply for it and what is the initiation procedure? | Reassessment initialization shall be the responsibility of the BSP. The BSP shall duly inform the TSO of one of the reasons for reassessment according to Chapter 2.2. After which, the TSO shall inform the BSP on the method by which the Reserve Unit may be re-qualified. | Baltic TSOs have provided clarification
Ignitis | Data exchange requirements provided in chapter 2.3. | 2 | The basic principles and requirements for data exchange should be transferred from the SOGL to this document and the stage at which they need to be developed should be specified. | The data exchange principles are based on SOGL and will be implemented by each TSO in the national terms and conditions. The technical data exchange requirements shall be implemented during the implementation stage of frequency restoration controller and the market data exchange shall be implemented in the market development stange when capacity and energy markets are established. | Baltic TSOs have provided clarification
National Energy Regulatory Council | Information required in the prequalification application provided in chapter 2.1. | 2 | In order to have more clarity for market participants, please explain Energy Identification Code (EIC) acronym in this document. | EIC abbreviation shall be defined in the document. | Document has been updated
Anonymous | Information required in the prequalification application provided in chapter 2.1. Is the information required from the market participant understood or additional clarification is needed on the information points? DISAGREE | 2 | We propose to add additional explanation regarding the General LFC reserve prequalification process (figure 1), for the case, when TSO themselves own and operate Reserve Units, giving a special attention on how to ensure a non discriminative approach to all BSP offering the Reserve Units. | Yes, TSO resources shall follow the same prequalifcation tests and need to fulfil the same requirements as other Reserve Units. TSO shall assess these requirements. It is the TSOs obligation to ensure that the connected Reserve Units are capable of providing reserves according to the requirements as TSO needs to use these to keep the balance of the system. | Baltic TSOs have provided clarification
Anonymous | General overview of the prequalification steps provided in chapter 2. Is the process acceptable for market participants? | 2 | Is there difference between qualification processes (or procedures) for capacity and energy markets, and is it possible to use reserve unit qualified for FCR in another reserve market (for example, aFRR)? | Reserve Units shall be prequalified to provide certain amount of service per service type. Prequalification is valid for both capacity and energy market for certain service type. Only units that are prequalified can participate in capacity and energy markets. Asset can prequalify for multiple service types and when providing service needs to make sure that the activation of all reserves should be possible according to the defined requirements. | Baltic TSOs have provided clarification
Anonymous | General overview of the prequalification steps provided in chapter 2. Is the process acceptable for market participants? | 2 | Is it possible, that BSP mandates qualification to its counterparty? | Prequalification is tied to a certain Reserve Unit. Any transfer of obligation to other Reserve Unit or BSP must have a separate successful prequalifcation for that Reserve Unit. | Baltic TSOs have provided clarification
Anonymous | General overview of the prequalification steps provided in chapter 2. Is the process acceptable for market participants? | 2 | What is qualification constraint (in MW) for smallest possible reserve unit for all reserve types (FCR, aFRR, mFRR)? | FCR shall have a minimum bid size of symmetrical 1 MW bid (+/- 1 MW in total band of 2 MW). aFRR and mFRR shall have a minimum bid size of either direction of 1 MW. | Baltic TSOs have provided clarification
Anonymous | General overview of the prequalification steps provided in chapter 2. Is the process acceptable for market participants? | 2 | From the document it was unclear how reserve's volumes will be determined and validated during prequalification steps. How long the tests should be? | The BSP defines the maximum volume they wish to prequalify. During the test the maximum capacity activation is tested according to each reserve type prequalification test. | Baltic TSOs have provided clarification
Anonymous | General overview of the prequalification steps provided in chapter 2. Is the process acceptable for market participants? | 2 | Is the BSP somehow remunerated for doing the prequalifications? | No the BSP shall not be compenstated for doing the prequalification. The energy that is planned to be activated during the prequalification test is added to the BSP schedule. If there are discrepencies from the planned schedule, that energy shall be counted as imbalance of the BSP. | Baltic TSOs have provided clarification
Anonymous | General overview of the prequalification steps provided in chapter 2. Is the process acceptable for market participants? | 2 | Is it possible to take a part of service providing after time of prequalification is ended, next year or even later? What is the forecasted final date/term for the end of prequalification’s process? | Prequalification will be a ongoing processes, where additional prequalifcation can be done as long there is market for LFC reserves. Prequalification shall be updated every 5 years according to SOGL. Only units that are prequalified can participate in the capacity and energy markets. Upon prequalification the Reserve Unit is free to provide services as long as the prequalification is valid. | Baltic TSOs have provided clarification
Anonymous | General overview of the prequalification steps provided in chapter 2. Is the process acceptable for market participants? | 2 | Page 6. Clause 2.1.4.3. Please specify the asked data on Z EIC, E EIC codes and assess those clarifications and validity? | Z and W EIC codes are required to manage Reserve Units. | Baltic TSOs have provided clarification
Anonymous | General overview of the prequalification steps provided in chapter 2. Is the process acceptable for market participants? | 2 | How often this document could be reviewed? | Baltic TSOs do not have plans on review the document periodically. The review of this document shall be done when there are updates in the SOGL, SAFA or other regulation requirements concerning prequalification of LFC reserves or the technical requirements for LFC reserves. | Baltic TSOs have provided clarification
Anonymous | Information required in the prequalification application provided in chapter 2.1. Is the information required from the market participant understood or additional clarification is needed on the information points? DISAGREE | 2 | Delivery point. How it will correlate with connection point/s in case of existing contract between TSO and producers (Contractors) within their authorities? Does the boundary changes?We propose to add paragraph 5.5. (at page 7) as following: “BSP shall have the right to dispute (challenge) the decision of TSO to reject the Reserve Unit and provide additional information for further evaluation”. | Measurement devices need only approval from TSOs and no boundary change is needed. For existing power plants delivery point will most likely be the same as currently available measurement devices. In case of impending rejection due to absence of required information, the TSO can extend the process by an additional 4 weeks and request the missing information. However, if the issue warranting rejection is not easily solvable, they may forgo this process and reject the Reserve Unit. | Baltic TSOs have provided clarification
Anonymous | Information required in the prequalification application provided in chapter 2.1. Is the information required from the market participant understood or additional clarification is needed on the information points? DISAGREE | 2 | It seems that virtual power plants (2.1.4.3. point allows not to provide EIC W information, which is only hard to do for virtual power plants, because contributing units changes all the time) also can provide FCR services and 2.1.5. point prescribes to ensure information about measuring equipment, in case of virtual power plant Delivery point most probably will be at TSO or DSO substation, in this case it is not clear if virtual power plant can use TSO/ DSO equipment or should install additional equipment. | In general data collection is responsibility of the BSP. In case TSO can identify measurement point which fulfils the requirements of Delivery point then conditions for Delivery Point are fulfilled and no additional equipment is needed to be installed. | Baltic TSOs have provided clarification
Anonymous | Information required in the prequalification application provided in chapter 2.1. Is the information required from the market participant understood or additional clarification is needed on the information points? DISAGREE | 2 | Please clarify 3.3. point. Will TSO themselves ensure data exchange with power plants? Will TSO invest to ensure data exchange with existing (according to RfG) power plants? | BSPs providing LFC service shall comply with the date exchange requirements and cover all BSP costs to establish the data exchange. No distinguish between existing and new installations according to RfG NC. | Baltic TSOs have provided clarification
Anonymous | General overview on the prequalification requirements provided in chapter 2.2. DISAGREE | 2 | It is not clear how these prequalification requirements could be applied in case of demand side response (how they shall be accepted to the grid)? If the reserve providing unit or group is connected to the DSO system, is it right that relevant BSP submits application still to TSO? Whether in this case there will be separate procedures from DSO side too? | Reserve Units connected to DSO are eligble to provide balancing services if they are able to successfully complete prequalication process. As different DSR models are being developed and used in Baltics and in Europe in general, Baltic TSOs agreed that DSR management shall be subject to requirements in the national terms and conditions. Baltic TSOs confirm that relevant BSP submits application to relevant TSO. | Baltic TSOs have provided clarification
Anonymous | Timeline presented in prequalification process provided in chapter 2.1. Are the time periods presented in the prequalification process acceptable? DISAGREE | 2 | We proposed to extended the prequalification period, giving the possibility to BSP to claim the decision of TSO to reject the Reserve Unit and provide additional information proving suitability of the Reserve Unit to provide corresponding reserves. | The time periods are defined according to SOGL Articles 155.3, 155.4, 159.3 and 159.4. In case of impending rejection due to absence of required information, the TSO can extend the process by an additional 4 weeks and request the missing information. However, if the issue warranting rejection is not easily solvable, they may forgo this process and reject the Reserve Unit. | Baltic TSOs have provided clarification
Anonymous | General overview on the prequalification requirements provided in chapter 2.2. DISAGREE | 2 | Article 182(3) of SO GL includes rule that the prequalification process shall have a maximum duration of 3 months from the submission of a complete formal application by the reserve providing unit or group. But in the chapter 2, prequalification process is assumed to be 20 weeks (or 4-5 months) long. Please explain why it is longer than specified in the SO GL | The SO GL Article 182(3) defines the time duration for the prequalification process after formal application is accepted by TSO. The first 8 weeks are forseen to complete formal application and after that 12 weeks for the prequalification testing and review of testing data. Baltic TSOs do not wish to prolong the process and will act as quick as possible. The time periods are defined according to SOGL Articles 155.3, 155.4, 159.3 and 159.4 | Baltic TSOs have provided clarification
Anonymous | General overview on the prequalification requirements provided in chapter 2.2. DISAGREE | 2 | Regarding to point 1, please clarify, if BSP holds grid test ( e.g. according to RfG), which is similar to LFC Reserve unit test, can this results be used to re-asses LFC Reserve unit qualification? (e.g. we have grid test in 2020 and 2025, but LFC test in 2022, should we make next test in 2027 or 2030, if tested parameters are same?) | During grid test there is no service amount defined. Therefore the prequalification for LFC reserves defines the available volumes. For the example if LFC prequalifcation is done in 2022, then re-assessment shall be done in 2027. Upon re-assessment of prequalification the Reserve Unit could be subject to simplified verification based on SO GL Article 155(5). | Baltic TSOs have provided clarification
Anonymous | General overview on the prequalification requirements provided in chapter 2.2. DISAGREE | 2 | Regarding to point 3, what is understand as "modernization", what are criteria of modernization? Is it possible to use the existing one connection point for both services (electricity, frequency) simultaneously? | Under modernization it is considered if any substantial part of the Reserve Unit or its governor control system is replaced/upgraded. Yes, multiple services can be provided simultaneously, but BSP needs to ensure that all simultaneously provided services are according to the defined requirements. For example, if both aFRR and mFRR are activated in the same direction then the ramping speed of both service types needs to be summed up to ensure that both services are provided within full activation time. | Baltic TSOs have provided clarification
Anonymous | General overview on the prequalification requirements provided in chapter 2.2. DISAGREE | 2 | Please clarify if a single RPU (RPG) can serve as FCR and FRR (aFRR, mFRR) service provider at the same time. | Yes. A Reserve Unit is eligable to prequalify in any variation of reserves as long as it maintains the same composition of technical units. | Baltic TSOs have provided clarification
Anonymous | Data exchange requirements provided in chapter 2.3. DISAGREE | 2 | It is not clear whether, in addition to references to the SO GL - 154(1), article 154(8), article 158(1)(e), article 158(4)(b), article 161(1)(f) and article 161(4)(b)), the BSP must comply also with the other data exchange provisions of the SO GL? For example, to those which is mentioned under Title 2 ("Data exchange") in SO GL? | Yes, as Baltic TSOs need to be compliant with SOGL then Baltic BSPs need to fulfil SOGL requirements. | Baltic TSOs have provided clarification
Anonymous | Data exchange requirements provided in chapter 2.3. DISAGREE | 2 | In chapter 2.1. point 3.3. is prescribed that TSO should ensure data exchange, in this chapter it seem like BSP should ensure data exchange. Who must invest in modernization of data communication? | BSPs providing LFC service shall comply with the date exchange requirements and cover all BSP costs to establish the data exchange. | Baltic TSOs have provided clarification
Anonymous | Data exchange requirements provided in chapter 2.3. DISAGREE | 2 | The service providing platforms (MARI, PASCAL or others) are needed to be installed before tendering? Does it requirement for prequalification? | BSPs will not be directly influenced by MARI or PICASSO. All bids submitted by BSP shall be shared with the appropriate platform through the BSP's connecting TSO. All prequalification requirements keep in mind the standards set by the respective platforms. Reserve Units that wish to participate in MARI and PICASSO platform need to be prequalified. MARI and PICASSO development is described by Baltic TSOs market documents. | Baltic TSOs have provided clarification
Anonymous | Data exchange requirements provided in chapter 2.3. DISAGREE | 2 | Page 8. Clause 2.3. Data exchange requirements. Please clarify the sense of subclause (sentence). | BSPs providing LFC service shall comply with the date exchange requirements and cover all BSP costs to establish the data exchange. | Baltic TSOs have provided clarification
Eesti Energia | General technical requirements for LFC reserve units provided in chapter 3. | 3 | It seems reasonable that the time periods in the Table 1 (3.1 Frequency ranges) are limited by MTU for each balancing service. Otherwise, older units, which have been connected to the grid before RfG requirements in Table 1 were published, only need to comply with the Grid Code requirements in force during their grid connection tests. | LFC is very important for operational security of power system. Following RfG frequency ranges and time periods ensures that reserve providing units are available during system disturbances. TSOs deem the RfG requirements to be realistic for most existing units. | Baltic TSOs have provided clarification
Eesti Energia | General technical requirements for LFC reserve units provided in chapter 3. | 3 | Accordingly, the same principle shall apply to 3.2 Voltage ranges, 3.3 Immunity to voltage disturbances and 3.4 ROCOF withstand capability. Again, derogations should be made for DSR and LER assets in VPP portfolio. | LFC is very important for operational security of power system. Following RfG requirements ensures that reserve providing units are available during system disturbances. TSOs deem the RfG requirements to be realistic for most existing units. DSR and LER assets need to follow the same requirements as defined based on the connection point voltage level. DCC article 28 defines requirements for DSR as following - DSR have the withstand capability to not disconnect from the system due to the rate-of-change-of-frequency up to a value specified by the relevant TSO. | Baltic TSOs have provided clarification
Eesti Energia | General technical requirements for LFC reserve units provided in chapter 3. | 3 | Regarding 3.5: Please describe how to define Delivery Points in a situation where an apartment building has only one Connection Point, but 20 residents living in this building have each their own 10 kW batteries to provide balancing services with. We propose that the Delivery Points of these batteries (Reserve Providing Units) are individual signal connections to the BSP’s VPP portfolio and the Delivery Point of the BSP’s VPP portfolio (Reserve Providing Group) is the signal connection to the TSO’s SCADA system. | Currently, all delivery points require a form of measurement approved by the TSO. Any additional requirements are set within national terms and conditions. | Baltic TSOs have provided clarification
Eesti Energia | General technical requirements for LFC reserve units provided in chapter 3. | 3 | Also, the only way to evaluate the quality of the service provided by fluctuating energy and load sources (they are often located far “behind the meter” as well), such as wind turbines, PV panels and demand side assets is by comparing their forecasted power/load levels (also called potential power) with their actual power/load levels. | Baltic TSOs agree in general with the approach, but detailed specifications for the approach needs to be developed in the future. | Baltic TSOs have provided clarification
Fusebox | General technical requirements for LFC reserve units provided in chapter 3. | 3 | What is the basis for the requirements used in chapter 3? Is it based on any other already functioning market or on an area with jointpower reserves? | Most of the requirements in chapter 3 are derived from COMMISSION REGULATION (EU) 2016/631 establishing a network code on requirements for grid connection of generators, COMMISSION REGULATION (EU) 2017/1485 establishing a guideline on electricity transmission system operation and COMMISSION REGULATION (EU) 2016/1388 establishing a Network Code on Demand Connection. | Baltic TSOs have provided clarification
Ignitis | General technical requirements for LFC reserve units provided in chapter 3. | 3 | The chapter no3 is not related to the prequalification requirements and shall be subject to requirements of connection to the grid. We suggest to remove the chapter “3. General technical requirements for LFC Reserve Units” from the document. | The LFC services have critical impact on system security in case of disturbances. TSOs need assurance that after major disturbance RPUs don't trip and increase the imbalance of the system. Fulfilment of these requirements ensures system security. | Baltic TSOs have provided clarification
National Energy Regulatory Council | Timeline presented in prequalification process provided in chapter 2.1. | 3 | TSOs could mention that in the time scale prolongation periode for 4 weeks is possible if additional information is needed from the potential FCR provder as it mentioned in 5.2 part of the document and in SOGL Article 155 (3). | TSOs note the comment and forsee that SO GL Article 155(3) is mentioned in the chapter 2.1 in point 5.2. | Baltic TSOs have provided clarification
National Energy Regulatory Council | Timeline presented in prequalification process provided in chapter 2.1. | 3 | According to SOGL Article 155 (5), reserve connecting TSO should recognise in prequalification process when compliance with certain requirements of SOGL have already been verified. NRA would ask TSOs to explain their actions in situations, where potential FCR provider has already met LFC reserves requirements. | No assets have been tested for LFC reserves in the Baltics. Once done so, the units that have prequalified shall be monitored and re-assessment of prequalification shall be done every 5 years or when there are substantial changes in the Reserve Unit according to SO GL Articles 155(6) and 159(6). Upon re-assessment of prequalification the Reserve Unit could be subject to simplified verification based on SO GL Article 155(5). | Baltic TSOs have provided clarification
Anonymous | General technical requirements for LFC reserve units provided in chapter 3. DISAGREE | 3 | Chapter 3.5 and explanatory note: Just to check if specified RPU and RPG alternatives takes Market participant's generation peculiarities into account. For example, if a unit has two units connected to transformer, or three units connected to transformer. | For Reserve Providing Units in parallel with common connection point need separate delivery points, each of which shall have measurement devices approved by the TSO. | Baltic TSOs have provided clarification
Anonymous | General technical requirements for LFC reserve units provided in chapter 3. DISAGREE | 3 | According to the COMMISSION REGULATION (EU) 2016/631 of 14 April 2016, RfG (article 3) the connection requirements set out in this Regulation shall apply to new power-generating modules. If TSO apply exactly the same requirements as in RfG wouldn’t there be limitations to existing generators? Neither RfG not DCC set requirements to BESS. | LFC is very important for operational security of power system. Following RfG requirements ensures that reserve providing units are available during system disturbances. TSOs deem the RfG requirements to be realistic for most existing units. There are no existing BESS in the Baltics and all new units shall be built based on the national grid codes. In context of requirements BESS will have mostly the same requirements as Power Park Modules. | Baltic TSOs have provided clarification
Anonymous | General technical requirements for LFC reserve units provided in chapter 3. DISAGREE | 3 | Besides that, in the Table 4, clearer references to national grid code requirements (specific articles, points) should be provided. | Please review each countries national grid code. | Baltic TSOs have provided clarification
Anonymous | General technical requirements for LFC reserve units provided in chapter 3. DISAGREE | 3 | Is article 12 (2) of DCC applied also to distribution (DSO)-connected demand facilities?What kind of Units or Reserve Provides Group is awaited and more highly preferred? | Baltic TSOs have no technological preference as long the Reserve Unit fulfils the set requirements. Article 12(2) of DCC is applicable to Transmission-Connected demand facilities, transmission-connected distribution facilities and distribution systems, and do not set requirements for distribution-connected demand facilities. Distribution connected demand facilities shall fulfil the national requirements and DCC Article 28, which sets special provisions for Reserve Units. | Baltic TSOs have provided clarification
Anonymous | General technical requirements for LFC reserve units provided in chapter 3. DISAGREE | 3 | Table 3: requirements set out in RfG tables 6.1. and 6.2. (voltage ranges) are applicable only for type D power-generating modules. Is it planned to apply it to all Reserve units? | Table has been updated to reflect RfG requirements. | Document has been updated
Anonymous | General technical requirements for LFC reserve units provided in chapter 3. DISAGREE | 3 | Page 10. Table 3. In row of 110 kV there is mentioned 30 min for both boundaries of p.u., but Reg. 2016/631 and “Tīkla kodekss elektroenerģijas nozarē” 21.clause determines that one of them is 20 min. Please clarify? | Table has been updated to reflect RfG requirements. | Document has been updated
Anonymous | General technical requirements for LFC reserve units provided in chapter 3. DISAGREE | 3 | Requirements for 110 kV connected BSP at voltage range 1.118 – 1.15 exceeds RfG requirements for type D units. Please clarify motivation to set such high requirements for LFC providing units. | Table has been updated to reflect RfG requirements. | Document has been updated
Anonymous | General technical requirements for LFC reserve units provided in chapter 3. DISAGREE | 3 | There should be defined requirements in case of simultaneous change of frequency and voltage. | Baltic TSOs do not define requirements for simultaneous changes of frequency or voltage. | Baltic TSOs have provided clarification
Anonymous | General technical requirements for LFC reserve units provided in chapter 3. DISAGREE | 3 | Table 4: requirements set out in RfG tables 7.1. and 7.2. (FRT requirements) are applicable only for type D power-generating modules. For type B requirements are slightly different, set out in tables 3.1. and 3.2. of RfG. RfG articles 14 3(a) and 16 3(a) set different requirements for B,C and D types. | Please review each countries national grid code. | Baltic TSOs have provided clarification
Anonymous | General technical requirements for LFC reserve units provided in chapter 3. DISAGREE | 3 | Voltage requirements are very strict, but it is unclear whether should they be complied at Connection point or at Delivery point? How it will be tested in case of RPG? For each unit of RPG separately? How virtual power plants will be tested? | Voltage requirements are applicable for Connection point. Testing of voltage requirements is not planned during the prequalification, assesment will be based on available information provided by BSP. | Baltic TSOs have provided clarification
Anonymous | General technical requirements for LFC reserve units provided in chapter 3. DISAGREE | 3 | In Latvia Grid code there are no requirements for voltage faults in grid below 110 kV. Will there be some changes in Latvian Grid code or it means that LFC providers in grid below 110 kV should not fulfill this requirement? | Units connected at voltage below 110 kV shall be compliant with national grid code requirements, as per Table 4. | Baltic TSOs have provided clarification
Anonymous | General technical requirements for LFC reserve units provided in chapter 3. DISAGREE | 3 | Is the similar approach regarding ROCOF is applied to all types of Reserve Units? | Yes, same ROCOF approach is applied to all Reserve Units. | Baltic TSOs have provided clarification
Anonymous | General technical requirements for LFC reserve units provided in chapter 3. DISAGREE | 3 | " Each Delivery Point can belong to only one Reserve Providing Unit or Reserve Providing Group ", does it mean, that in case if delivery point is DSO or TSO substation, only one RPU/RPG can use it? Or substation will be divided in connection points? How delivery points are set for demand side response, when the Aggregator have multiple locations? If BSP wants to add additional power generating module or demand unit to its "portfolio", is it necessarily to go through prequalification procedures again for all "portfolio", or only for "new" generating module or demand unit? | DSO or TSO substation can be a connection point for the Reserve Unit, but the Reserve Unit must have a separate delivery point on which the service provision can be accurately measured by the TSO or BSP must be able to submit aggregated data for technical enities below 1,5 MW. As different DSR models are being developed and used in Baltics and in Europe in general, Baltic TSOs agreed that DSR management shall be subject to requirements in the national terms and conditions. | Baltic TSOs have provided clarification
Anonymous | General technical requirements for LFC reserve units provided in chapter 3. DISAGREE | 3 | If BSP wants to add additional power generating module or demand unit to its "portfolio", is it necessarily to go through prequalification procedures again for all "portfolio", or only for "new" generating module or demand unit? | Reserve Providing Group composition change is managed as stated in 4.4.3., 5.4.3. and 5.8.3., technical entities per definition cannot be tested independantly, and thus need to prequalify along with the entire RPG; Gen. modules, demand units and technical enitites connected to a common connection point may prequalify separately and later be simply added to the existing RPG. BSP assets that can fulfil the LFC service requirements should be prequalified separately. | Baltic TSOs have provided clarification
Anonymous | FCR service technical requirements provided in chapter 4.2. DISAGREE | 4 | What voltage level in chapter 4.1. point 3 correspond to HV, MV and LV? Previously only 330 kV, 110 kV and <110kV were mentioned. | Text is updated. Voltages 330 kV, 110 kV and <110kV are considered. | Document has been updated
Anonymous | FCR service technical requirements provided in chapter 4.2. DISAGREE | 4 | Please clarify 4.2.1. statement " The proportional activation is negative: as the frequency deviation increases, the power output of the FCR provider shall decrease and vice versa. " Deviation can be both negative and positive, so it seem it is wrong wording, in case if frequency grows above 50Hz, power output of generating modules shall decrease? For demand response it shall be opposite operation, which is not stated in 4.2.1.? | Wording is improved to reflect the DSR reaction to FCR. | Document has been updated
Anonymous | Additional requirements for FCR providing groups provided in chapter 4.4. DISAGREE | 4 | Chapter 4.4. does not make clear how mentioned RPGs will fulfill requirements of chapter 3 and how it will be tested? | Chapter 3 requirements apply to all technical entities and Reserve Providing Units within the RPG and shall be verified based on available documentation provided by the BSP. Chapter 2 shall be amended to list the necessary data TSO requires for verification. | Document has been updated
Fusebox | Is the FCR real-time signal list description in chapter 4.2.5 sufficient and understandable? | 4 | 4.2.5 states that real time data should be provided to TSO with atime resolution of at least 10s. Is it “real time” data within 10second packages or is it metering data with 10s resolution? | TSOs have updated the explanation of real-time and timestamped data exchange possibilities. | Document has been updated
Eesti Energia | FCR service technical requirements provided in chapter 4.2. | 4 | 4.2.2: The accuracy requirement 1% of the maximum capacity is ok for power plants but not realistic for demand side response and fluctuating renewable energy assets. With reference to Directive 2019/944 Article 17 Section 2, we propose to use 0.1 MW accuracy for assets <10 MW instead. | Service accuracy shall be at least +/- 0,1 MW or +/- 10% of the maximum LFC service volume that is prequalified, whichever is larger, if not defined differently in the national terms and conditions or other legislation. DSR units shall be a RPU or RPG and the same rules apply. The inaccuracy of measurements shall not exceed 2% achieved either by direct measurement using a meter of 1.0 class (B class) or indirect using a measurement transformer and meter of class 0.5 (C class) each, if not defined differently in the national terms and conditions or other legislation. | Document has been updated
Eesti Energia | FCR service technical requirements provided in chapter 4.2. | 4 | Regarding 4.1: The requirement that every FCR provider locally measures the frequency deviation seems to be impossible to comply with in case smaller DSR assets are aggregated together in VPP portfolio, thereby violating the Directive 2019/944 Article 17 Section 2. In this case, derogation must be made so, that only the VPP portfolio as the Reserve Providing Group should measure the frequency and distribute the control signals to the Reserve Units in the portfolio. | In accordance of SO GL Article 154.9, Baltic TSOs allow the use of centralized frequency measurement for FCR groups with a prequalified FCR capacity < 1.5 MW. If a BSP decides to prequalify several FCR groups < 1.5 MW using centralized frequency measurement, a different frequency meter must be used for each concerned FCR group for redundancy reasons. For any other FCR group, Baltic TSOs require as per product definition local frequency measurement on each delivery point within that FCR group. | Baltic TSOs have provided clarification
Eesti Energia | Additional requirements for FCR providing groups provided in chapter 4.4. | 4 | As was mentioned before in response to chapter 4.1 (row 7), the requirement that every distributed asset should be able to measure frequency deviation itself and act accordingly, is technically difficult to realize and therefore is in conflict with Directive 2019/944 Article 17 Section 2. | In accordance of SO GL Article 154.9, Baltic TSOs allow the use of centralized frequency measurement for FCR groups with a prequalified FCR capacity < 1.5 MW. If a BSP decides to prequalify several FCR groups < 1.5 MW using centralized frequency measurement, a different frequency meter must be used for each concerned FCR group for redundancy reasons. For any other FCR group, Baltic TSOs require as per product definition local frequency measurement on each delivery point within that FCR group. | Baltic TSOs have provided clarification
Eesti Energia | FCR service technical requirements provided in chapter 4.2. | 4 | For a VPP portfolio consisting of fluctuating renewable energy sources and/or demand side assets, occasional exemptions to the linear or monotonic piecewise linear power-frequency characteristic are necessary due to forecasting inaccuracies. | Baltic TSOs agree in general with the approach, but detailed specifications for the approach needs to be developed in the future. | Baltic TSOs have provided clarification
Eesti Energia | FCR service technical requirements provided in chapter 4.2. | 4 | 4.2: We suggest rephrasing the FCR start of activation requirement in accordance with RfG: the activation of active power frequency response by the power-generating module shall not be unduly delayed. In the event of any delay greater than two seconds, the power-generating facility owner shall justify it to the relevant TSO. It does not mean that the start of activation can not be longer than 2 seconds! We see that TSOs should approach this on case by case basis, based on the national grid codes that were effective during the grid acceptance tests of the specific power plant. For example, in the Estonian grid code that was effective during the Auvere PP grid connection, it was required (§261 section (6)) that 50% of the primary reserve would be activated within 10 seconds and 100% within 30 seconds, and the power plant must be capable of providing it at least for 15 minutes. | Chapter 4.2.1 includes the wording proposed. No intentional delays are allowed and if the active power frequency response is greater than 2 seconds then it is required to demonstrate the technical reason. Technical reasons shall be assessed by TSO case by case. | Baltic TSOs have provided clarification
Eesti Energia | FCR service technical requirements provided in chapter 4.2. | 4 | 4.2.3: According to SOGL Article 156(4), “An FCR provider shall guarantee the continuous availability of FCR, with the exception of a forced outage of a FCR providing unit, during the period of time in which it is obliged to provide FCR.” As per Estonian national Grid Code §261 section (6) that was effective during the grid connection of Auvere PP, a power plant had to be capable of offering primary reserve at least for 15 minutes. Therefore, we suggest rephrasing or removing the sentence “A potential long-lasting unidirectional frequency deviation shall be covered by FCR providers without limitation.” | As the SOGL Article 156(4) highlights, FCR provider shall gurantee continous availability of FCR. When prequalifing FCR capacity, FCR providing unit must take into account the SOGL requirement and make sure the FCR provision is ensured as required. | Baltic TSOs have provided clarification
Eesti Energia | Additional requirements for Limiter Energy Reservoir (LER) FCR providers provided in chapter 4.3. | 4 | We understand that assets that have an energy reservoir of only 15 minutes or 1 hour can also be deemed as LER and provide FCR service. | An asset qualifying for FCR LER status shall be able to ensure continuous FCR provision in either direction for no less than 30 minutes and no more than 2 hours without any sort of active energy reservoir management at full qualified power capacity. An asset that can only provide 15 minutes of FCR (less than 30 minutes) in either direction is not eligible FCR provider. | Baltic TSOs have provided clarification
Eesti Energia | FCR prequalification tests provided in chapter 4.5. | 4 | 4.5.1.4 (Accuracy of frequency control) and 4.5.2.4 (Overshoots): We propose that the accuracy of both is 1% of installed capacity for larger power plants (>=10 MW) and 0.1 MW for assets <10 MW or alternatively +/-10% band as is the rule in Nordic SA (Nordic System Operation Agreement – Annex LFCR). | Service accuracy shall be at least +/- 0,1 MW or +/- 10% of the maximum LFC service volume that is prequalified, whichever is larger, if not defined differently in the national terms and conditions or other legislation. DSR units shall be a RPU or RPG and the same rules apply. The inaccuracy of measurements shall not exceed 2% achieved either by direct measurement using a meter of 1.0 class (B class) or indirect using a measurement transformer and meter of class 0.5 (C class) each, if not defined differently in the national terms and conditions or other legislation. | Document has been updated
Eesti Energia | Additional requirements for FCR providing groups provided in chapter 4.4. | 4 | BSPs can define the list of assets in their portfolio, but this does not mean that all these assets take part in reserve provision. | During prequalifcation the maximum bid capacity is checked. It is the BSP's discretion which combination of assets in the Reserve Unit shall provide the procured volume. During energy bid creation the BSP must take into account the available assets. In case energy bid does not correspond to actual activation, TSO can monitor the service provision and in case of violation may fine and terminate the prequalification for Reserve Unit. | Baltic TSOs have provided clarification
Eesti Energia | Additional requirements for FCR providing groups provided in chapter 4.4. | 4 | It should be possible to add/remove or replace assets in the portfolio after the prequalification test has been done without causing the need to carry out the prequalification tests again. Please see the approach and wording used in Elering-Fingrid aFRR pilot documents (Standard contract and Appendix 1). | As different DSR models are being developed and used in Baltics and in Europe in general, Baltic TSOs agreed that DSR management shall be subject to requirements in the national terms and conditions. | Baltic TSOs have provided clarification
Eesti Energia | Additional requirements for FCR providing groups provided in chapter 4.4. | 4 | 4.4.4: Time resolution of 10 seconds in unfeasible for smaller demand side response assets. With reference to Directive 2019/944 Article 17 Section 2, we propose a derogation that only the VPP portfolio as the Reserve Providing Group needs to provide 10 second data of the portfolio (as a black box) and additionally larger assets (>= 1,5 MW) in the portfolio, but not the assets that are <1,5 MW. Please see the approach and wording used in Elering-Fingrid aFRR pilot documents (Standard contract and Appendix 1). | Real-time requirements are according to SOGL Article 50(1), 154(8), 154(9) and 158(1)(e). Reserves providing units or a reserve providing group shall be monitord on real-time measurements. Aggregated assets in RPU aor RPG shall provide real-time measurements, but individual assets in the RPG or RPU that are below 1,5 MW do not need to have real-time data exchange established. | Baltic TSOs have provided clarification
Eesti Energia | Is the FCR real-time signal list description in chapter 4.2.5 sufficient and understandable? | 4 | We suggest amending the “Scheduled active power output” so that for fluctuating energy sources and demand side assets it can be based on forecasts. | In large TSOs would agree with proposal to include the forecasts for scheduled active power output for fluctuation energy sources and demand side assets. The final requirements for the forecasts will be defined by each TSO in the national implementation. | Baltic TSOs have provided clarification
Eesti Energia | FCR prequalification tests provided in chapter 4.5. | 4 | We propose that testing method will be “tailor-made” to best match the technical possibilities of the assets. | Tailored testing method would give way to unfair testing between different resources and therefore Baltic TSOs foresee common testing principles for all technologies that provide LFC reserves. The described testing principles are a general guideline and should be realistic for all LFC Reserve Units. | Baltic TSOs have provided clarification
Fusebox | FCR service technical requirements provided in chapter 4.2. | 4 | Hard to understand following: 1) maximum duration for technical entities?2) Are demand side load reserves qualified as limited energy reserve? 3) Smallest MTUbid size? | 1) The maximum duration is not defined, only the minimum period which is needed to ensure system security. 2.)If the BSP's Reserve Unit is capable of providing reserves, unaided by any energy reservoir management methodology, for more than 2 hours (or cannot do so for at least 30 minutes), the Reserve unit is not considered an LER. 3.)The smallest permitted bid size is 1 MW. | Baltic TSOs have provided clarification
Fusebox | Additional requirements for Limiter Energy Reservoir (LER) FCR providers provided in chapter 4.3. | 4 | 4.3 states that LER FCR provider has 2 hours of capacity at full continuous activation. However, 4.3.2 states that minimum in alert state is 30 minutes. How should LER FCR provider dimension its reservoirs? Power to energy ratio 1:2,5? | LER FCR providers shall provide their reserves upon entering Alert State for at least 30 minutes. An FCR LER energy capacity shall have a supply of 30 minutes up to 2h of full qualified activation. LER FCR providers may only qualify up to 80% of their rated power to ensure the provision of TminLER in Alert State according to document [https://eepublicdownloads.entsoe.eu/clean-documents/nc-tasks/EBGL/SOGL_A118_A154(2)_190322_Additional%20Properties%20of%20FCR_All%20TSO's%20CE_final%20submission_Explanatory%20Note.pdf] | Baltic TSOs have provided clarification
Fusebox | FCR prequalification tests provided in chapter 4.5. | 4 | Maybe in addition provide some prequalification test templates for FCR providers.ItCould be “prequalification for prequalification test”and in order to speed up the verification process. | TSOs can develop and provide prequalification test templates within development of national terms and conditions. National terms and conditions shall be developed by latest at end of Q4 2022. | Baltic TSOs have provided clarification
Ignitis | FCR prequalification tests provided in chapter 4.5. | 4 | LER FCR providing unit or LER FCR providing groups depending on technology used for service shall have different testing programs. Could you please describe how the equal conditions and nondiscriminatory and transparency will be ensured? Will the standard terms and conditions for the testing will be available publicly? | According to "All CE TSOs’ proposal for additional properties of FCR in accordance with Article 154(2) of the Commission Regulation (EU) 2017/1485 of 2 August 2017 establishing a guideline on electricity transmission system operation", FCR LERs shall have more lenient requirements on account of their limited energy reservoir, however, this entitles the TSO to issue tests on whether the minimum requirements set are adhered to. | Baltic TSOs have provided clarification
Ignitis | FCR prequalification tests provided in chapter 4.5. | 4 | Please specify how the electricity generated during the testing period will be accounted for? | The energy that is planned to be activated during the prequalification test is added to the BSP schedule. If there are discrepencies from the planned schedule, that energy shall be counted as imbalance of the BSP. | Baltic TSOs have provided clarification
Anonymous | FCR prequalification tests provided in chapter 4.5. DISAGREE | 4 | How to exclude the conflict of interest, when the prequalification tests are needed for LER (BESS) operated by TSO, if the counterpart of the process is the same TSO responsible for the LFC Area? TSO will perform this tests publicly ? | Yes, TSO resources shall follow the same prequalifcation tests and need to fulfil the same requirements as other Reserve Units. TSO shall assess these requirements. It is the TSOs obligation to ensure that the connected Reserve Units are capable of providing reserves according to the requirements as TSO needs to use these to keep the balance of the system. | Baltic TSOs have provided clarification
Anonymous | FCR service technical requirements provided in chapter 4.2. DISAGREE | 4 | Please clarify figure 2, is it true that 1.0 p.u. of activation should correspond to droop level? Or 1 p.u. is value which RU declared for FCR service? | 1 p.u. is the maximum declared FCR volume that is procured. | Baltic TSOs have provided clarification
Anonymous | FCR service technical requirements provided in chapter 4.2. DISAGREE | 4 | FCR provision of RPU (MW) at certain frequency deviation is dependent on droop setting and Pmax of power-generating module. Please clarify if BSP is free to select droop setting for frequency deviations within range of ±200 mHz to provide FCR reserve based on placed bid size (MW).Please clarify if term FCR reserve is applicable to power (MW) deliveries of RPU within ±200 mHz or additional power delivered outside FSM range (±200 mHz ) is also considered FCR reserve as chapter 4.2.4 says: "FCR provision in case of large frequency transients and emergency state". | BSP can set the droop setting as they need to ensure that full capacity of FCR service is provided wihtin +/- 200 mHz range. TSO expects the full activation of the prequalified FCR volume within the +/- 200 mHz range. Outside +/- 200 mHz range is not considered FCR provision. | Baltic TSOs have provided clarification
Anonymous | FCR service technical requirements provided in chapter 4.2. DISAGREE | 4 | It is understood that support of the stability of the frequency requirement for frequency deviations greater than ±200 mHz (LFSM-U &LFSM-O) is also relevant to other connected power-generating modules according to national grid code and not necessarily RPUs. In that case we don't see any added value to have it additionally defined in this document. Please clarify figure 4 and figure 5, it seems like FCR provider shall not activate any active power deviation prior frequency deviation is greater than 200 mHz.. Illustration of figure 4 and figure 5 doesn't correspond to FCR situation (FSM activated). | During provision of FCR service, Reserve Units shall provide LFSM-O and LFSM-U (up to the technical capability limits of the equipment). When Reserve Unit is not providing the FCR, the requirements of respective Grid Codes apply. Figures 4 and 5 specify the LFSM functionality which shall be cumulative to FCR service (FCR service activation ends at 200 mHz deviation and LFSM activation starts at 200 mHz deviation). | Baltic TSOs have provided clarification
Anonymous | FCR service technical requirements provided in chapter 4.2. DISAGREE | 4 | Figure 3: It corresponds to RfG requirement set for type C power-generating modules (RfG article 15, table 5). Is it applicable to all Reserve Units? | Figure 2 and 3 show the most important properties of FCR service and are applicable to all FCR providing units. | Baltic TSOs have provided clarification
Anonymous | FCR service technical requirements provided in chapter 4.2. DISAGREE | 4 | Figure 4: LFSM-O corresponds to RfG requirement set for type A power-generating modules (RfG article 13, figure 1). Is it applicable to all Reserve Units? | LFSM-O requirements defined in the RfG article 13 are applicable for all types of PGMs, namely A, B, C and D. | Baltic TSOs have provided clarification
Anonymous | FCR service technical requirements provided in chapter 4.2. DISAGREE | 4 | Figure 5: LFSM-U corresponds to RfG requirement set for type B power-generating modules (RfG article 14, figure 4). Is it applicable to all Reserve Units? | LFSM-U requirements are for C and D type units | Baltic TSOs have provided clarification
Anonymous | FCR service technical requirements provided in chapter 4.2. DISAGREE | 4 | According to RfG the droop settings shall be between 2 % and 12 %. Why 5%? | Droop value of 5% stated in 4.2.4. refers to default droop of LFSM operation coordinated by Baltic TSOs and it shall be applied if no other instructions from TSO are provided. | Baltic TSOs have provided clarification
Anonymous | FCR service technical requirements provided in chapter 4.2. DISAGREE | 4 | Please clarify figure 4 and figure 5, it seem like FCR provider shall not activate any active power deviation prior frequency deviation is greater than 200 mHz. | FSM requirements are cumulative to LFSM mode. FCR activation is done in the ranges of +/- 200 mHz and LFSM activation is beyond +/- 200 mHz. If FCR provision is inactive, only LFSM response is required. | Baltic TSOs have provided clarification
Anonymous | FCR service technical requirements provided in chapter 4.2. DISAGREE | 4 | What are connecting TSO requirements on communication interface. Is resolution 10 s and accuracy of measurements of the 0,5 class is Ok? | The inaccuracy of measurements shall not exceed 2% achieved either by direct measurement using a meter of 1.0 class (B class) or indirect using a measurement transformer and meter of class 0.5 (C class) each, if not defined differently in the national terms and conditions or other legislation. | Baltic TSOs have provided clarification
Anonymous | FCR service technical requirements provided in chapter 4.2. DISAGREE | 4 | Page 17. Clause 4.2.3. says communicate as soon as possible if service doesn’t ensured. Please be more specific and determine mining of “ASAP”? | The requirement is derived from SO GL Article 158.4. SO GL doesn't provide more specific requirement. | Baltic TSOs have provided clarification
Anonymous | FCR service technical requirements provided in chapter 4.2. DISAGREE | 4 | 4.2.6. Please clarify if the statement :" It means that an FCR provider can be considered connected to only one TSO " also means that BSP can trade FCR reserves only to the TSO it is physically connected to? This is not clearly defined and explained. | SOGL Article 154(5) defines that each FCR provider shall have only one reserve connecting TSO. FCR service provision to different TSOs is possible via TSO-TSO model and will be described more thouroughly in the Baltic capacity market document. | Baltic TSOs have provided clarification
Anonymous | Additional requirements for Limiter Energy Reservoir (LER) FCR providers provided in chapter 4.3. DISAGREE | 4 | Does it mean that Daugava HPP if they are capable to provide FCR for more than 2 hours without complete depletion of reservoir are not considered as LER FCR providers? Please clarify first sentence of 4.3. chapter, full continuous activation of its FCR for a period of 2 hours might lead or leads to limitation? | Baltic TSOs consider scenario where Daugava HPPs are not able to provide FCR for more than 2 hours unrealistic and thus Daugava HPPs are not considered as LER. | Baltic TSOs have provided clarification
Anonymous | Additional requirements for Limiter Energy Reservoir (LER) FCR providers provided in chapter 4.3. DISAGREE | 4 | If BESS is used for provision of FCR the full capacity utilization time is not necessary for 2 hours, as FCR activations are intermittent in nature and not always maximum in amplitude. For example, for 10 MW BESS 5-7 MWh storage capacity is enough to provide FCR. | Yes, in normal situation the FCR activation is intermittent, but system might experience long lasting unidirectional frequency deviations. Continuous provision of FCR for 2 h is not required from LER RPU/RPG, but for the definition of LER RPU (RPU which is able to provide full activation of FCR for more than 2 hours is not considered LER). However, other limitations apply as per 4.3.2. | Baltic TSOs have provided clarification
Anonymous | Additional requirements for Limiter Energy Reservoir (LER) FCR providers provided in chapter 4.3. DISAGREE | 4 | In the chapter 4.3.2. it is necessary to explain what does a continuous FCR full activation for a time period no less than 30 minutes means. It does not mean that for example BESS shall be available with maximum charge or discharge capacity continuously for 30 min. | Continous FCR full activation for time period of 30 minutes means that FCR providing unit shall be able to provide full FCR service unidirectionally for 30 minutes period. | Baltic TSOs have provided clarification
Anonymous | Additional requirements for Limiter Energy Reservoir (LER) FCR providers provided in chapter 4.3. DISAGREE | 4 | It is important to harmonize the technical requirements for the planned BESS projects. For now, it is not clear why FCR should be provided at least 30 min. How does it correlate with the previously mentioned requirement to provide FCR for 15 min? As well, the minimum time between continuous activations of FCR is not defined. This greatly affects the choice of the required BESS capacity for the projects. | Any FCR provider is expected to maintain normal operation within Normal State. Upon entering Alert State, LER FCR providers are expected to Operate for at least 30 minutes, after which, they are obliged to resort to enter Reserve Mode. After depletion of the LER's reservoir, it must return to normal operation within 2h. There is no minimum delay between subsequent activations. | Baltic TSOs have provided clarification
Anonymous | Additional requirements for Limiter Energy Reservoir (LER) FCR providers provided in chapter 4.3. DISAGREE | 4 | 2017/1485 SO GL 156(9) states, that FCR should be not less 15 min and no longer 30 min. During previous public consultations Baltic TSO did not give any specific indications about time frame (only that it should be between 15 and 30 min) of FCR, despite fact that 2017/1485 SO GL 156(11) requirements. In December 2020 Baltic TSO published "Baltic Load-Frequency Control block concept document " where was no information about FCR full activation period. In March 2021 Baltic TSO published " Baltic reserve capacity market study" where was no information about FCR full activation period. In document presented during this consultation is first time when market participants get noticed that FCR time should be not less than 30 min for LER BSP, which affect projects regarding to LER development in Baltic states. We would like to stress out that Latvian TSO definitely knew this LER FCR limitations (30 min, not 15min) prior any other party that legally could provide LER FCR service. Most probably Latvian TSO knew this limitation even prior getting government acceptance of support for BESS installation and in such way has even greater influence on FCR provision market in Latvia. | According to the Latvian Grid Code (Amendment 7, Clause 14.8), the unit shall be able to provide FCR for at least 30 minutes. Thus, in order to ensure equality among market participants, it was decided that LERs must also adhere to these rules. | Baltic TSOs have provided clarification
Anonymous | Additional requirements for Limiter Energy Reservoir (LER) FCR providers provided in chapter 4.3. DISAGREE | 4 | Please provide documentation mentioned in SO GL 156(11). Proposed rules will force market participants to change plans regarding LER which will demand additional time and costs prior project realization. | The documentation mentiond can be found - https://consultations.entsoe.eu/system-operations/rgce-fcr-with-ler-sogl-156-11/ | Baltic TSOs have provided clarification
Anonymous | Additional requirements for Limiter Energy Reservoir (LER) FCR providers provided in chapter 4.3. DISAGREE | 4 | Please clarify figure 7, for example if provided FCR power is 2MW, and SOC is 50% LER should store 2MWh, if SOC decrease to 20% LER should store 4.8MWh? Also, it is unclear demand for 3 hours storage capability at 85% SOC, according to chapter 4.3. LER is, if FCR provider is limited to provide FCR full activation for less than 2 hours. In such case, it is no more LER, because can store energy for more than 2 hours. Figure 7 is very confusing; requirement should be explained in more common way. It should be easy to understand scale of LER to provide predefined FCR to the market. | Figure 7 illustrates that an LER can continue to participate in the energy market and submit further bids only under the circumstance that it has enough energy stored for 30 minutes (the minimum period of delivery under Alert State). | Baltic TSOs have provided clarification
Anonymous | Additional requirements for Limiter Energy Reservoir (LER) FCR providers provided in chapter 4.3. DISAGREE | 4 | One more question for Figure 7. If SOC is 50%, declared FCR is 2 MW, then LER should store 2MWh. In same time FCR is required for 30 minutes, which means that 1.25 MWh (in case of BESS even 1.15MWh is enough to ensure BESS healthy SOC) is more than enough to provide 2MW for 30 minutes, what is reason to demand 2MWh storage capability from LER at 50% SOC and 4MWh at 100% SOC? | Example - if an LER with prequalified power of 10 MW (nominal power at least 12,5 MW) and an energy to power ratio of 2 (meaning 20 MWh) is at a SoC under 25% (5 MWh) or over 75% (15 MWh), it is not permitted to continue participating in the FCR market for the next MTUs until it regains a SoC that allows for provision of FCR for 30 minutes under Alert State. | Baltic TSOs have provided clarification
Anonymous | Additional requirements for Limiter Energy Reservoir (LER) FCR providers provided in chapter 4.3. DISAGREE | 4 | Where this requirement comes from: FCR with LER shall have a ratio of rated power to the prequalified FCR of at least 1.25:1? In other words it means that LER FCR shall always have 25% reserve margin to committed FCR power. Why should TSO have this reserve for the reserve? It is rated power of LER, not capacity (energy in MWh), if this additional 25% of installed power is not activated, what is reason for it? | According to "All CE TSOs’ proposal for additional properties of FCR in accordance with Article 154(2) of the Commission Regulation (EU) 2017/1485 of 2 August 2017 establishing a guideline on electricity transmission system operation" referred to in the chapter 4.3.3. The limitation on rated power ensures that the BSP has a guarenteed reserve of power with which to restore the LER's SoC in case simultaneous activation and SoC management are in the same direction (exceeding 100% of qualified power). | Baltic TSOs have provided clarification
Anonymous | Additional requirements for Limiter Energy Reservoir (LER) FCR providers provided in chapter 4.3. DISAGREE | 4 | Demand on energy capacity and power of FCR LER should be technically and economically based, studies should be provided for market participants. It might lead to much higher FCR service prices, if market participants should invest in 2MW/4MWh LER and be capable to sell only 1.6MW FCR, which could be understood from requirements commented above. | Definitions of LER FCR providers, and limitations set on them are based on "All CE TSOs’ proposal for additional properties of FCR in accordance with Article 154(2) of the Commission Regulation (EU) 2017/1485 of 2 August 2017 establishing a guideline on electricity transmission system operation" and the accompanying explanatory note. Link to the document - https://eepublicdownloads.entsoe.eu/clean-documents/nc-tasks/EBGL/SOGL_A118_A154(2)_190322_Additional%20Properties%20of%20FCR_All%20TSO%27s%20CE_final%20submission_Explanatory%20Note.pdf | Baltic TSOs have provided clarification
Anonymous | Additional requirements for Limiter Energy Reservoir (LER) FCR providers provided in chapter 4.3. DISAGREE | 4 | At present document time between possible FCR activation is not mentioned, which is critical to choose right power of LER. | No time limitations are to be set on time between subsequent activations. | Baltic TSOs have provided clarification
Anonymous | Additional requirements for FCR providing groups provided in chapter 4.4. DISAGREE | 4 | Does statement " FCR provision can be provided by technical entities that cannot comply alone with the FCR service technical requirements." Mean that any reserve unit which can comply alone with the FCR service technical requirements cannot be a part of RPG? | Yes. If the unit is technically capable of independantly providing the service, it should be prequalified as a RPU. | Baltic TSOs have provided clarification
Anonymous | Additional requirements for FCR providing groups provided in chapter 4.4. DISAGREE | 4 | Chapter 4.4.1. Isn’t the requirement for technical entities in additional to centralized system have also local activiation and decentralized frequency measurements for each particular entity / connection point (an autonomous FCR activation capability) is exaggerated especially in the case of demand response? | In accordance of SO GL Article 154.9, Baltic TSOs allow the use of centralized frequency measurement for FCR groups with a prequalified FCR capacity < 1.5 MW. If a BSP decides to prequalify several FCR groups < 1.5 MW using centralized frequency measurement, a different frequency meter must be used for each concerned FCR group for redundancy reasons. For any other FCR group, Baltic TSOs require as per product definition local frequency measurement on each delivery point within that FCR group. | Baltic TSOs have provided clarification
Anonymous | Additional requirements for FCR providing groups provided in chapter 4.4. DISAGREE | 4 | Chapter 4.4.2. We propose to add the requirement “FCR providing groups and Reserve Providing Units shall be independent of Baltic TSO”. | Not relevant for LFC reserve prequalification technical requirements. | Not relevant for LFC reserve prequalification technical requirements.
Anonymous | Additional requirements for FCR providing groups provided in chapter 4.4. DISAGREE | 4 | Chapter 4.4.3. the procedure of composition change for FCR providing groups not very transparent and complex. We have an impression that any change of the composition shall go through the prequalification process. | Baltic TSOs see the compostion change requirements justified for situation where the maximum capacity of the RPG will change. Except in the case where the capacity is decreased by removing a technical entity from the RPG and the capacity of technical entity can be clearly identified. Both RPUs and RPGs follow the same requirements for new prequalification when the maximum capacity for service is changed. | Baltic TSOs have provided clarification
Anonymous | Additional requirements for FCR providing groups provided in chapter 4.4. DISAGREE | 4 | Chapter 4.4.4. It is not clear why 1.5 MW threshold is used to get the right to aggregate the real-time data for more than one technical entity. | Real-time requirements are according to SO GL Article 154(8) and 154(9), which allow to aggregate all units that have power less than 1,5 MW. Only units over 1,5 MW need to have individual measurements according to SO GL requirements. | Baltic TSOs have provided clarification
Anonymous | Is the FCR real-time signal list description in chapter 4.2.5 sufficient and understandable? | 4 | More or less sufficient and understandable. Not all the parameters indicated in the table 5 might be needed for the FCR LER (figure 6, chapter 4.3.4.). For example, active power output. | Baltic TSOs do not agree with indication as to estimate FCR provision the measured active power output must be measured also for FCR LER units. | Baltic TSOs have provided clarification
Anonymous | FCR prequalification tests provided in chapter 4.5. DISAGREE | 4 | Does chapter 4.5. correspond to point 4 of figure 1? | Yes prequalification tests correspond to organisation of the prequlification test step in Figure 1. | Baltic TSOs have provided clarification
Anonymous | FCR prequalification tests provided in chapter 4.5. DISAGREE | 4 | Chapter 4.5. does not provide any information of qualification according to chapter 3 requirements. | The Chapter 3 requirements are not specifically tested during qualification, and will be evaluated using available information provided by the BSP. | Baltic TSOs have provided clarification
Anonymous | FCR prequalification tests provided in chapter 4.5. DISAGREE | 4 | Explanation of LFC area and LFC block could be added to the chapter 1.2. | The LFC area and LFC block are defined in the LFC concept document which is linked in this document chapter 1. | Baltic TSOs have provided clarification
Anonymous | FCR prequalification tests provided in chapter 4.5. DISAGREE | 4 | 4.5.1.3. Please clarify, it seems that sampling rate of 1s also is acceptable. Should it be at least 1 sample per 100ms? | Sampling rate of 100 ms shall be used for measurements during prequalification testing only. | Baltic TSOs have provided clarification
Anonymous | FCR prequalification tests provided in chapter 4.5. DISAGREE | 4 | 4.5.2.2. Is there any requirements for droop settings? | Droop setting for FCR provision shall correspond to at least the amount of FCR to be qualified. The droop shall be configured to fulfil requirements stated in Chapter 4 to provide full provision in case of frequency deviation of +/- 200 mHz. | Baltic TSOs have provided clarification
Anonymous | FCR prequalification tests provided in chapter 4.5. DISAGREE | 4 | 4.5.2.4 Is there any time limits for overshoot? E.g. it can be above 10% for several seconds, is it acceptable? | The requirements are updated. | Document has been updated
Anonymous | FCR prequalification tests provided in chapter 4.5. DISAGREE | 4 | Please clarify if tests mentioned in 4.5.1 and 4.5.2. should be performed for LER units too? What are requirements for LER state in case if they should be performed? In case if such tests should not be performed for LER, please explain why? | Yes, these tests are also meant for LERs. However, while testing, LER limitations shall be taken into account (e.g. duration of activation during dynamic test). 4.5.3. describes tests additional to the ones in 4.5.1. and 4.5.2. | Baltic TSOs have provided clarification
Anonymous | FCR prequalification tests provided in chapter 4.5. DISAGREE | 4 | Please specify the measuring point of all tests mentioned in paper? Is it one common point – CP&DP? For example like in offered case 1 and case 2. | Measurements of delivery points shall be used during the prequalification testing and will be used for the continous monitoring of service provision. | Baltic TSOs have provided clarification
Anonymous | FCR prequalification tests provided in chapter 4.5. DISAGREE | 4 | If the LFC (FCR, FRR) measuring points are else from delivery points, which actions will be asked in case of measuring result distortion and no validations? | We are not expecting to have situation when delivery points differ from the measurement points. Referring to the paragrph 3.5 The Delivery point shall have the network configuration and associated measurement equipment allowing TSO to fully control the provision of the LFC reserves, as well referring to the paragraph 2.1.5. Information about Delivery points including the data on measurement transformers, measuring equipment and data connections shall be provided for TSO. | Baltic TSOs have provided clarification
Anonymous | aFRR service technical requirements provided in chapter 5.3. | 5 | What does the 1 MTU (market time unit) means? What time period will be MTU for aFRR? | The validity period for aFRR capacity bids shall be 15 minutes. Longer description of the MTU shall be provided in the document. | Document has been updated
Anonymous | mFRR service technical requirements provided in chapter 5.7. | 5 | What does the 1 MTU (market time unit). What time period will be MTU for mFRR? | The validity period for mFRR capacity bids shall be 15 minutes. Longer description of the MTU shall be provided in the document. | Document has been updated
Eesti Energia | Is the mFRR data requirement list description in chapter 5.7.5 sufficient and understandable? | 5 | Real-time and periodically real time data must be defined. With reference to Directive 2019/944 Article 17 Section 2, we propose once in 1 minute for smaller assets (<1.5 MW) that communicate over API and data aggregation possibility. | Aggregated assets in RPU or RPG shall provide aggregated real-time measurement, but individual assets in the RPG or RPU that are below 1,5 MW do not need to have real-time data exchange established, but timestamped data will be collected. The solution how to collect timestamped data shall be developed by each TSO. | Document has been updated
Anonymous | aFRR service technical requirements provided in chapter 5.3. | 5 | Should aFRR providers comply with chapter 3. requirements? If not, why? This service will be activated at lower frequencies than FCR. Please clarify LV, MV, HV limits. | Chapter 3 is applicable for all types of LFC reserves. aFRR providers shall comply with requirements set in Chapter 3. LV, MV, HV limits are updated in the document. | Document has been updated
Eesti Energia | Additional requirements for aFRR providing groups provided in chapter 5.4. | 5 | As mentioned previously, it must be possible to change (add/remove/replace) the composition of VPP portfolio after the prequalification tests. Please see the approach and wording used in Elering-Fingrid aFRR pilot documents (Standard contract and Appendix 1). | As different DSR models are being developed and used in Baltics and in Europe in general, Baltic TSOs agreed that DSR management shall be subject to requirements in the national terms and conditions. | Baltic TSOs have provided clarification
Eesti Energia | aFRR service technical requirements provided in chapter 5.3. | 5 | 5.3.5.: We would welcome the initiative to standardize the communication architecture and interfaces of Baltic TSOs. In addition to that, we propose using a single common portal for the trading messages and only using the destination country/TSO as one parameter in the message signal list. | The real-time communication ends up on the SCADA-BSP communication, as each TSO can have different SCADA system, this cannot be standardized more than using same communication standards. The common portal for capacity market is not the topic for harmonised LFC reserve prequalification requirements and shall be covered by the market related communication and documents. | Baltic TSOs have provided clarification
Eesti Energia | aFRR service technical requirements provided in chapter 5.3. | 5 | With reference to Directive 2019/944 Article 17 Section 2, we propose once in 1 minute for smaller assets (<1.5 MW) that communicate over API and data aggregation possibility. | Aggregated assets in RPU or RPG shall provide aggregated real-time measurement, but individual assets in the RPG or RPU that are below 1,5 MW do not need to have real-time data exchange established, but timestamped data will be collected. The solution how to collect timestamped data shall be developed by each TSO. | Baltic TSOs have provided clarification
Eesti Energia | Additional requirements for aFRR providing groups provided in chapter 5.4. | 5 | Please explain the difference of clauses 3 in 5.4.2 and 2 in 5.4.3. | Clause 3 of 5.4.2. states that two already independant RPGs cannot be combined into one RPG. However, clause 2 of 5.4.3. adds that an RPU can be added to an existing RPG. | Baltic TSOs have provided clarification
Eesti Energia | aFRR prequalification tests provided in chapter 5.5. | 5 | 5.5.3 and 5.5.4: Activation tolerance +/-5% is unrealistic especially when the provided service is e.g. 1 MW. | Service accuracy shall be at least +/- 0,1 MW or +/- 10% of the maximum LFC service volume that is prequalified, whichever is larger, if not defined differently in the national terms and conditions or other legislation. DSR units shall be a RPU or RPG and the same rules apply. The inaccuracy of measurements shall not exceed 2% achieved either by direct measurement using a meter of 1.0 class (B class) or indirect using a measurement transformer and meter of class 0.5 (C class) each, if not defined differently in the national terms and conditions or other legislation. | Document has been updated
Eesti Energia | Is the aFRR real-time signal list description in chapter 5.3.5 sufficient and understandable? | 5 | 5.3.5: We would welcome the initiative to standardize the communication architecture and interfaces of Baltic TSOs. In addition to that, we propose using a single common portal for the trading messages and only using the destination country/TSO as one parameter in the message signal list. | The real-time communication ends up on the SCADA-BSP communication, as each TSO can have different SCADA system, this cannot be standardized more than using same communication standards. The common portal for capacity market is not the topic for harmonised LFC reserve prequalification requirements and shall be covered by the market related communication and documents. | Baltic TSOs have provided clarification
Eesti Energia | Is the aFRR real-time signal list description in chapter 5.3.5 sufficient and understandable? | 5 | With reference to Directive 2019/944 Article 17 Section 2, we propose once in 1 minute for smaller assets (<1.5 MW) that communicate over API and data aggregation possibility. | Aggregated assets in RPU or RPG shall provide aggregated real-time measurement, but individual assets in the RPG or RPU that are below 1,5 MW do not need to have real-time data exchange established, but timestamped data will be collected. The solution how to collect timestamped data shall be developed by each TSO. | Baltic TSOs have provided clarification
Eesti Energia | aFRR prequalification tests provided in chapter 5.5. | 5 | We propose that the accuracy/activation tolerance is 1% of installed capacity for larger power plants (>=10 MW) and 0.1 MW for assets <10 MW or alternatively +/-10% band as is the rule in Nordic SA (Nordic System Operation Agreement – Annex LFCR). | Service accuracy shall be at least +/- 0,1 MW or +/- 10% of the maximum LFC service volume that is prequalified, whichever is larger, if not defined differently in the national terms and conditions or other legislation. DSR units shall be a RPU or RPG and the same rules apply. The inaccuracy of measurements shall not exceed 2% achieved either by direct measurement using a meter of 1.0 class (B class) or indirect using a measurement transformer and meter of class 0.5 (C class) each, if not defined differently in the national terms and conditions or other legislation. | Document has been updated
Eesti Energia | mFRR service technical requirements provided in chapter 5.7. | 5 | 5.7.3: We propose that the accuracy is 1% of installed capacity for larger power plants (>=10 MW) and 0.1 MW for assets <10 MW or alternatively +/-10% band as is the rule in Nordic SA (Nordic System Operation Agreement – Annex LFCR). | Service accuracy shall be at least +/- 0,1 MW or +/- 10% of the maximum LFC service volume that is prequalified, whichever is larger, if not defined differently in the national terms and conditions or other legislation. DSR units shall be a RPU or RPG and the same rules apply. The inaccuracy of measurements shall not exceed 2% achieved either by direct measurement using a meter of 1.0 class (B class) or indirect using a measurement transformer and meter of class 0.5 (C class) each, if not defined differently in the national terms and conditions or other legislation. | Document has been updated
Eesti Energia | Additional requirements for mFRR providing groups provided in chapter 5.8. | 5 | As mentioned previously, it must be possible to change (add/remove/replace) the composition of VPP portfolio after the prequalification tests. Please see the approach and wording used in Elering-Fingrid aFRR pilot documents (Standard contract and Appendix 1). | As different DSR models are being developed and used in Baltics and in Europe in general, Baltic TSOs agreed that DSR management shall be subject to requirements in the national terms and conditions. | Baltic TSOs have provided clarification
Eesti Energia | mFRR service technical requirements provided in chapter 5.7. | 5 | 5.7.4: We understand that it is not a requirement for a LER to be able to provide mFRR service for at least 2 hours (energy reservoir can also be sized according to the MTU). | No restrictions are imposed on mFRR LERs, however, they are subject to the rules set for conventional reserve providers. | Baltic TSOs have provided clarification
Eesti Energia | mFRR service technical requirements provided in chapter 5.7. | 5 | 5.7.5: We would welcome the initiative to standardize the communication interfaces of Baltic TSOs. | The real-time communication ends up on the SCADA-BSP communication, as each TSO can have different SCADA system, this cannot be standardized more than using same communication standards. The common portal for capacity market is not the topic for harmonised LFC reserve prequalification requirements and shall be covered by the market related communication and documents. | Baltic TSOs have provided clarification
Eesti Energia | mFRR prequalification tests provided in chapter 5.9. | 5 | 5.9.3 and 5.9.4: Activation tolerance +/-5% is unrealistic especially when the provided service is e.g. 1 MW. | Service accuracy shall be at least +/- 0,1 MW or +/- 10% of the maximum LFC service volume that is prequalified, whichever is larger, if not defined differently in the national terms and conditions or other legislation. DSR units shall be a RPU or RPG and the same rules apply. The inaccuracy of measurements shall not exceed 2% achieved either by direct measurement using a meter of 1.0 class (B class) or indirect using a measurement transformer and meter of class 0.5 (C class) each, if not defined differently in the national terms and conditions or other legislation. | Document has been updated
Fusebox | aFRR service technical requirements provided in chapter 5.3. | 5 | Is the minimum bid size still 1MW. Chapter 5.3.2 is a bit confusing “The resolution of the signal used by the aFRR providing unit to define the quantity of aFRR to be activated shall be at least 0,1 MW, unless defined differently in the national implementation of FRC.” | aFRR bids shall be fully divisible, where minimum bid size is 1 MW and the resolution of the activation signal is 0,1 MW, unless defined differently on national implementation of FRC. | Baltic TSOs have provided clarification
National Energy Regulatory Council | Data exchange requirements provided in chapter 2.3. | 5 | NRA would like to note that SOGL Article 161 is about minimal technical requirements of RR. As it is understud and stated in LFC concept document Baltic TSOs do not intend to introduce RR both on Baltic States level or on the national level. | Yes, Baltic TSOs do not intend introducing RR in the Baltics. If any Baltic TSO wishes to introduce RR in the future, then it is up to that TSO. | Baltic TSOs have provided clarification
National Energy Regulatory Council | Data exchange requirements provided in chapter 2.3. | 5 | NRA would ask TSOs to expand their position about requirements for communication. Where these requirements will be specified? What security masures are foreseen for communication requirements? | Specification for TSOs on common FRC parameters for monitoring and control shall be set in currently ongoing Consultancy on requirements for implementation of automatic Frequency Restoration Controllers in Baltic Power systems. These requirements shall be implement into national regulation considering Frequency Restoration Controllers desing and recomendations from Consultancy. Frequency Restoration Controller shall have same cyber security requirements as SCADA system. | Baltic TSOs have provided clarification
National Energy Regulatory Council | Data exchange requirements provided in chapter 2.3. | 5 | NRA would like to ask TSOs to explain at the document what are the procedures if potential FCR provider is connected to DSO network. What data exchange schemes are foreseen with DSO and potential FCR provider? | The BSP using assets within DSO network needs to ensure that appropriate measurements are available and collected. It is BSPs obligation to provided required data to TSOs. Data transmission requirements shall be implemented by each TSO. | Baltic TSOs have provided clarification
Anonymous | aFRR service technical requirements provided in chapter 5.3. | 5 | Chapter 5.3.1. What is the basis for determined aFRR activation parameters (activation time 30 s, full deployment 5 min.)? | European standard energy and capacity aFRR product that will be used in the energy platfrom PICASSO. | Baltic TSOs have provided clarification
Anonymous | aFRR service technical requirements provided in chapter 5.3. | 5 | What are requirements for FRR LER providers? Nothing mentioned, like it was in chapter 4.3. How FRR LER provider can assume what amount of FRR it will be allowed to provide, will it be TSO decision? | There are no concrete reccomendations from CE TSOs on operation of LERs for FRR, they will operate under the same conditions that conventional power gen. modules do. LER FRR providers shall need to fulfil the requirements defined in chapters 5.3.4 and 5.7.4. Delivery responsibility of the BSP will be defined in the FRR market rules. | Baltic TSOs have provided clarification
Anonymous | Additional requirements for aFRR providing groups provided in chapter 5.4. | 5 | Chapter 5.4.2. We propose to add the requirement “aFRR providing groups and Reserve Providing Units shall be independent of Baltic TSO”. | Not relevant for LFC reserve prequalification technical requirements. | Not relevant for LFC reserve prequalification technical requirements.
Anonymous | Additional requirements for aFRR providing groups provided in chapter 5.4. | 5 | Chapter 5.4.4. It is not clear why 1.5 MW threshold is used to get the right to aggregate the real-time data for more than one technical entity. | Real-time requirements are according to SO GL Article 158(1)(e), which allow to aggregate all units that have power less than 1,5 MW. Only units over 1,5 MW need to have individual measurements according to SO GL requirements. | Baltic TSOs have provided clarification
Anonymous | Additional requirements for aFRR providing groups provided in chapter 5.4. | 5 | Can entity which is part of FCR providing group be a part of aFRR providing group? | No units or entities shall be able to be part of multiple groups simultaneously. However, the same group (consisting of the same units and entities) may be prequalified for multiple services - FCR, mFRR, aFRR. | Baltic TSOs have provided clarification
Anonymous | Additional requirements for aFRR providing groups provided in chapter 5.4. | 5 | In chapter 5.4.4. is mentioned that data according 5.3.4 should be provided, should data have mentioned in 5.3.5. be provided as well? | Yes, the reference has been not updated. The correct reference is 5.3.5. | Document has been updated
Anonymous | Is the aFRR real-time signal list description in chapter 5.3.5 sufficient and understandable? | 5 | More or less sufficient and understandable. Shall potential aFRR providing unit provide TSO real time data on TSO signal confirmation and signal connectivity confirmation? | Specification for TSOs on common FRC parameters for monitoring and control shall be set in currently ongoing Consultancy on requirements for implementation of automatic Frequency Restoration Controllers in Baltic Power systems. These requirements shall be implement into national regulation considering Frequency Restoration Controllers desing and recomendations from Consultancy. | Baltic TSOs have provided clarification
Anonymous | aFRR prequalification tests provided in chapter 5.5. | 5 | Chapter 5.5.1. How to exclude the conflict of interest, when the prequalification tests are needed for BESS operated by TSO, if the counterpart of the process is the reserve connecting TSO? | Yes, TSO resources shall follow the same prequalifcation tests and need to fulfil the same requirements as other Reserve Units. TSO shall assess these requirements. It is the TSOs obligation to ensure that the connected Reserve Units are capable of providing reserves according to the requirements as TSO needs to use these to keep the balance of the system. | Baltic TSOs have provided clarification
Anonymous | aFRR prequalification tests provided in chapter 5.5. | 5 | Chapter 5.5.4. How this requirement “aFRR capacity shall not deviate more than 5% of the maximum service value” was defined? | Baltic TSOs foresee the accuracy of the service as following - Service accuracy shall be at least +/- 0,1 MW or +/- 10% of the maximum LFC service volume that is prequalified, whichever is larger, if not defined differently in the national terms and conditions or other legislation. DSR units shall be a RPU or RPG and the same rules apply. Baltic TSOs foresee that this accuracy level shall ensure the quality of the services. | Baltic TSOs have provided clarification
Anonymous | aFRR prequalification tests provided in chapter 5.5. | 5 | In 2021 Baltic TSO published " Baltic reserve capacity market study" indicate aFRR upwards, and downwards service, testing procedure foresees test of both regimes, thus, some service providers could efficiently provide only one type of activation upwards/downwards. In our opinion, testing conditions should be split according to activation type, to ensure greater number of service provision parties, which will lead to lower service prices. | Chapter 5.5.1 states that in case asymmetrical aFRR service is provided then the testing schedule shall be updated to reflect the maximum upward and downward step separataly. | Baltic TSOs have provided clarification
Anonymous | mFRR service technical requirements provided in chapter 5.7. | 5 | In the chapter 5.3.1 Activation of aFRR the PICASSO platform was mentioned, while in the chapter 5.7.1. Activation of mFRR the MARI platform was NOT mentioned. Why? | The aFRR activation via PICASSO shall be corrected by the PICASSO activation optimisation function results that will modify the local activation based on MOL. The mFRR activation via MARI shall provide certain infomration which specific bids TSO needs to activate. | Baltic TSOs have provided clarification
Anonymous | mFRR service technical requirements provided in chapter 5.7. | 5 | What is the basis for determined mFRR activation parameters (activation time 7 min., FAT 12,5 min, deactivation period 10 min.)? | European standard energy and capacity mFRR product that will be used in the energy platfrom MARI. | Baltic TSOs have provided clarification
Anonymous | mFRR service technical requirements provided in chapter 5.7. | 5 | If mFRR activation command is provided by email or web service, when 7 minute activation preparation time starts? Same with deactivation. | The mFRR activation preparation time starts when the signal for activation was received. Service deactivation depends on the MTU length, for MARI implementation the MTU is 15 minute. This is further described in the "Baltic mFRR balancing solution implementation for operation with MARI platform" document. | Baltic TSOs have provided clarification
Anonymous | mFRR service technical requirements provided in chapter 5.7. | 5 | Why in 5.7.5. chapter table aFRR providing unit is mentioned? | Baltic TSOs mistake, mFRR is considered | Document has been updated
Anonymous | mFRR service technical requirements provided in chapter 5.7. | 5 | Please clarify if the statement :" mFRR provider can be considered connected to only one TSO " also means that BSP can trade mFRR reserves only to the TSO it is physically connected to? This is not clearly defined and explained. | SOGL Article 158(1)(a) defines that each FRR provider shall have only one reserve connecting TSO. FRR service provision to different TSOs is possible via TSO-TSO model and will be described more thouroughly in the Baltic capacity market document. | Baltic TSOs have provided clarification
Anonymous | Additional requirements for mFRR providing groups provided in chapter 5.8. | 5 | Chapter 5.8.2. We propose to add the requirement “mFRR providing groups and Reserve Providing Units shall be independent of Baltic TSO”. | Not relevant for LFC reserve prequalification technical requirements. | Not relevant for LFC reserve prequalification technical requirements.
Anonymous | Additional requirements for mFRR providing groups provided in chapter 5.8. | 5 | Chapter 5.8.4. It is not clear why 1.5 MW threshold is used to get the right to aggregate the real-time data for more than one technical entity. | Real-time requirements are according to SO GL Article 158(1)(e), which allow to aggregate all units that have power less than 1,5 MW. Only units over 1,5 MW need to have individual measurements according to SO GL requirements. | Baltic TSOs have provided clarification
Anonymous | Additional requirements for mFRR providing groups provided in chapter 5.8. | 5 | Can entity which is part of FCR or aFRR providing group be a part of mFRR providing group? | No units or entities shall be able to be part of multiple groups simultaneously. However, the same group (consisting of the same units and entities) may be prequalified for multiple services - FCR, mFRR, aFRR. | Baltic TSOs have provided clarification
Anonymous | Additional requirements for mFRR providing groups provided in chapter 5.8. | 5 | In chapter 5.8.4. is mentioned that data according 5.7.4 should be provided, should data have mentioned in 5.7.5. be provided as well? | Yes, the reference has been not updated. The correct reference is 5.7.5. | Baltic TSOs have provided clarification
Anonymous | Is the mFRR data requirement list description in chapter 5.7.5 sufficient and understandable? | 5 | In the chapter 5.7.1. it is mentioned that communication from TSO to mFRR providing unit could be provided by phone, email or web service. Why only in the case of web service activation, TSO is obliged to send data to the mFRR providing unit? Shouldn’t it be the only requirement to make activation only through the web service activation? | Baltic TSOs correct the requirement that web service activation shall be forwarded to the BSP and not mFRR providing unit. It is expected that BSP shall make the mFRR activation as needed. All listed activation methods are available. | Baltic TSOs have provided clarification
Anonymous | mFRR prequalification tests provided in chapter 5.9. | 5 | Chapter 5.9.1. How to exclude the conflict of interest, when the prequalification tests are needed for BESS operated by TSO, if the tests can be carried out ONLY after TSO has given its formal approval to the testing procedures? | Yes, TSO resources shall follow the same prequalifcation tests and need to fulfil the same requirements as other Reserve Units. TSO shall assess these requirements. It is the TSOs obligation to ensure that the connected Reserve Units are capable of providing reserves according to the requirements as TSO needs to use these to keep the balance of the system. | Baltic TSOs have provided clarification
Anonymous | aFRR prequalification tests provided in chapter 5.5. | 5 | In 2021 Baltic TSO published " Baltic reserve capacity market study" indicate mFRR upwards, and downwards service, testing procedure foresees test of both regimes, thus, some service providers could efficiently provide only one type of activation upwards/downwards. In our opinion, testing conditions should be split according to activation type, to ensure greater number of service provision parties, which will lead to lower service prices. | Chapter 5.9.1 states that in case asymmetrical mFRR service is provided then the testing schedule shall be updated to reflect the maximum upward and downward step separataly. | Baltic TSOs have provided clarification
Anonymous | mFRR prequalification tests provided in chapter 5.9. | 5 | Chapter 5.9.4. How other parameters used in prequalifiactions tests in addition to those mentioned in the chapter 5.7.1. (for example, activation tolerance of +/- 5%, activated energy volume at least 80% during timeframe of T+7 to T+22, activated energy supplied by the mFRR providing unit does not exceed 120% during timeframe of T+0 to T+27,5) are defined? | Baltic TSOs foresee that by applying defined parameters to the mFRR service prequalification ensures the quality of mFRR service provision. | Baltic TSOs have provided clarification
National Energy Regulatory Council | aFRR service technical requirements provided in chapter 5.3. | 12 | In order to have more clarity for market participants, NRA would ask to provide more information on market time unit (MTU) and what MTUs are for each balancing energy products. | Based on the implementation and development of 15 minute ISP (Imbalance settlement period) and 15 minute MTU projects, it is foreseen that the LFC services shall have a validity period of 15 minutes for both capacity and energy bids. Longer description of the MTU and Validity period is provided in the document. | Document has been updated
Eesti Energia | General comment | gen | Do Reserve Units, that are capable of providing FCR service also in case the deviation exceeds +/-200 mHz, get additional compensation for that extra benefit? | Given question is not relevant for harmonised principles for Baltic LFC reserve prequalifcation, but shall be covered by the Baltic LFC market rules. | Not relevant for LFC reserve prequalification technical requirements.
Ignitis | General comments | gen | 4.5.1.3 Testing method. The test is carried out simulating fictitious frequency ramps within the control system of the potential FCR providing unit or group of units….. What will be group of unit testing methodology? | Same methodology as for single FCR providing unit. The simulated frequency steps shall be provided to the agreed system or frequency steps are simulated within BSP system to reflect how the FCR group activation shall be performed. | Baltic TSOs have provided clarification
Ignitis | General comments | gen | The document shall be improved by adding the clear procedures and terms for the preparation, testing, evaluation, and acceptance. The principles shall be extended and clarified in more detailed way by adding the clear procedures. There is no clear understanding how the equal conditions and transparency among Baltic TSOs will be implemented to ensure the equal treatment of market participants and comply with the harmonized requirements for LFC block reserve capacity. | The service agreement and national terms and conditions shall be developed based on the Baltic harmonised LFC reserve prequalifcation requirements, which will ensure harmonised requirements for all Baltic market participants. | Baltic TSOs have provided clarification
Ignitis | General comments | gen | 4.5.1.3 ….It is required to measure active power response and simulating frequencies with at least 100 ms sample rate…… Will it really be enough to register power response and simulating frequencies? | Yes, Baltic TSOs foresee the sample rate to be enough to validate FCR provision quality. | Baltic TSOs have provided clarification
Ignitis | General comments | gen | 5.3.5 Real time data requirement for aFRR service provider. The data exchange standard and/or protocol shall be defined and described into document. | Each TSO can have a different frequency restoration controller implementation which can set different requirements on data exchange. | Baltic TSOs have provided clarification
Anonymous | General comments | gen. | Inclusion of Latvian and Lithuanian TSO's own BESS projects in the Investment Request of the Baltic synchronization project phase II creates additional uncertainty for other possible market participants about the development of the capacity reserve market and reserve pricing mechanisms. Furthermore, the Directive (EU) 2019/944 states that TSOs may operate their reserve providing units (e.g. batteries) if balancing capacity services on the market cannot be provided by other market participants at a reasonable price. However, it is not clearly defined, what price levels the TSOs will consider reasonable. | Not relevant for LFC reserve prequalification technical requirements. | Not relevant for LFC reserve prequalification technical requirements.
Anonymous | General comments | gen. | These uncertainties burden the incentives of market participants to develop their reserve providing units or services by adding the risks to ensure the profitability and utility of their reserve providing projects. | Not relevant for LFC reserve prequalification technical requirements. | Not relevant for LFC reserve prequalification technical requirements.
Anonymous | General comments | gen. | Initiative of TSO to develop electricity storage batteries and to provide capacity reserves must be performed under strict Latvian and European legislation ensuring the transparent and competitive capacity reserve market for all market participants. Intervention of TSO to market operation with its own reserve capabilities shall be prohibited. | Not relevant for LFC reserve prequalification technical requirements. | Not relevant for LFC reserve prequalification technical requirements.
Anonymous | General comments | gen. | Is it available the Draft of further service contract? | The service agreement and national terms and conditions shall be developed for each TSO after the finalised Baltic harmonised LFC reserve prequalifcation principles. | Baltic TSOs have provided clarification
Anonymous | General comments | gen. | Does it clearly defined the minimum and maximum annual amount of each business service (FCR, FRR)? | The volume of FCR capacities shall be fixed annualy by the CESA FCR sharing key and will be procured throughout the year. For aFRR and mFRR the capacities shall be dependent on the latest FRR dimensioning calculation output, which is done according to the FRR dimensioning methodology developed by Baltic TSOs for the Baltic LFC block .The annual volume of FCR, aFRR and mFRR activation is dependent on the imbalance of the system. There is no set minimum and maximum volume of services that will be activated. | Baltic TSOs have provided clarification
Anonymous | General comments | gen. | Market participant is planning to provide reserve capacity services in all market segments by its existing generating units, as well it is considering installation of battery energy storage system (BESS) to further enhance its regulating capabilities. Inclusion of Latvian and Lithuanian TSO's own BESS projects in the Investment Request of the Baltic synchronization project phase II creates additional uncertainty for other possible market participants about the development of the capacity reserve market and reserve pricing mechanisms. Furthermore, the Directive (EU) 2019/944 states that TSOs may operate their reserve providing units (e.g. batteries) if balancing capacity services on the market cannot be provided by other market participants at a reasonable price. However, it is not clearly defined, what price levels the TSOs will consider reasonable. These uncertainties burden the incentives of market participants to develop their reserve providing units or services by adding the risks to ensure the profitability and utility of their reserve providing projects. Initiative of TSO to develop electricity storage batteries and to provide capacity reserves must be performed under strict Latvian and European legislation ensuring the transparent and competitive capacity reserve market for all market participants. Intervention of TSO to market operation with its own reserve capabilities shall be prohibited. | Not relevant for LFC reserve prequalification technical requirements. | Not relevant for LFC reserve prequalification technical requirements.
Anonymous | General comments | gen. | It is not clear, how TSO are planning to ensure transparency and non discrimination of competitive bidding process, when some of them are planning to participate in this process with own Reserve Units? How the potential market participants could be sure that TSO intervention into the ancillary service markets would not distort the competition? | Not relevant for LFC reserve prequalification technical requirements. | Not relevant for LFC reserve prequalification technical requirements.
Anonymous | General comments | gen. | Please explain, how cross-border reserve trading will be organised? Will there be the similar approach as in Nord Pool power exchange, where market participants could bid only in their respective price zone, while cross-country exchange is implemented in the power exchange as an implicit auctions (market splitting), taking into account NTC (Net Transfer Capacity). Will the prequalification process be organised similarly in all three countries with harmonised rules and procedures? | Yes, prequalification process shall organised similarly in all Baltic countries based on the harmonised principles for Baltic LFC reserve prequalifcation, but the cross-border reserve trading is not relevant for the given document and shall be covered by the Baltic LFC market rules and capacity market documents. | Not relevant for LFC reserve prequalification technical requirements.